## Sheet1
This section covers power piping systems in steam-generating, central-heating, and industrial plants. Power piping systems include all steam, water, and oil piping within, or forming part of these plants, except certain portions under the jurisdiction of the ASME Boiler Code.
ASA B31 Section: |  |  |  | Power Piping District Heating Piping |  |  | Power Piping | [5 empty] | Industrial Gas and Air
Seamless Pipe Specification: |  |  |  | A-106-B Carbon Steel |  |  | A-335-P11 and P22 Alloy Steel |  |  |  |  | A-335-P22 | A-106-B
Weld Fittings Specification: |  |  |  | A-234-WPB Carbon Steel |  |  | A-234-WP11 and WP22 Alloy Steel |  |  |  |  | A-234-WP22 | A-234-WPB
Nominal Pipe Size | Wall Thickness |  |  | Temperature (deg. F) |  |  | Temperature (deg. F) |  |  |  |  | Temp. (deg. F) | Temperature (deg. F)
| I.P.S. | Schedule No. | Inches | -20 to 650 | 700 | 750 | 800 | 850 | 900 | 950 | 1000 | 1050 | 100 | 450
1/2" | STD | 40 | 0.109 | 1103 | 1055 | 952 | 1103 | 1059 | 963 | 815 | 586 | 436 | 2371 | 2055
| XS | 80 | 0.147 | 2434 | 2328 | 2101 | 2434 | 2337 | 2126 | 1814 | 1330 | 989 | 4250 | 3684
|  | 160 | 0.188 | 3904 | 3735 | 3371 | 3904 | 3748 | 3410 | 2940 | 2202 | 1637 | 6371 | 5522
| XXS |  | 0.294 | 8389 | 8026 | 7243 | 8389 | 8054 | 7327 | 6517 | 5242 | 3898 | 12911 | 11189
3/4" | STD | 40 | 0.113 | 997 | 954 | 861 | 997 | 957 | 871 | 736 | 529 | 393 | 2031 | 1760
| XS | 80 | 0.154 | 2113 | 2021 | 1824 | 2113 | 2028 | 1845 | 1571 | 1147 | 853 | 3625 | 3141
|  | 160 | 0.219 | 3982 | 3809 | 3438 | 3982 | 3823 | 3478 | 3000 | 2250 | 1673 | 6306 | 5465
| XXS |  | 0.308 | 6941 | 6640 | 5993 | 6941 | 6664 | 6062 | 5337 | 4191 | 3117 | 10544 | 9138
1" | STD | 40 | 0.133 | 1200 | 1148 | 1036 | 1200 | 1152 | 1048 | 887 | 639 | 475 | 2209 | 1915
| XS | 80 | 0.179 | 2222 | 2125 | 1918 | 2222 | 2133 | 1940 | 1654 | 1209 | 899 | 3641 | 3156
|  | 160 | 0.25 | 3873 | 3705 | 3344 | 3873 | 3718 | 3382 | 2915 | 2183 | 1623 | 6006 | 5205
| XXS |  | 0.358 | 6658 | 6369 | 5748 | 6658 | 6391 | 5814 | 5109 | 3994 | 2970 | 10011 | 8676
1 1/4" | STD | 40 | 0.14 | 1059 | 1013 | 914 | 1059 | 1017 | 925 | 782 | 563 | 418 | 1901 | 1647
| XS | 80 | 0.191 | 1939 | 1855 | 1674 | 1939 | 1861 | 1693 | 1440 | 1049 | 780 | 3142 | 2723
|  | 160 | 0.25 | 3006 | 2876 | 2595 | 3006 | 2886 | 2625 | 2249 | 1663 | 1237 | 4647 | 4028
| XXS |  | 0.382 | 5585 | 5343 | 4821 | 5585 | 5361 | 4877 | 4254 | 3269 | 2431 | 8333 | 7222
1 1/2" | STD | 40 | 0.145 | 1005 | 962 | 868 | 1005 | 965 | 878 | 742 | 533 | 397 | 1756 | 1522
| XS | 80 | 0.2 | 1821 | 1742 | 1572 | 1821 | 1748 | 1591 | 1352 | 983 | 731 | 2917 | 2528
|  | 160 | 0.281 | 3093 | 2959 | 2671 | 3093 | 2970 | 2702 | 2316 | 1715 | 1275 | 4719 | 4090
| XXS |  | 0.4 | 5114 | 4893 | 4415 | 5114 | 4910 | 4466 | 3883 | 2962 | 2203 | 7589 | 6577
2" | STD | 40 | 0.154 | 905 | 866 | 781 | 905 | 869 | 791 | 668 | 479 | 356 | 1544 | 1338
| XS | 80 | 0.218 | 1661 | 1589 | 1434 | 1661 | 1595 | 1451 | 1232 | 894 | 664 | 2612 | 2264
|  | 160 | 0.344 | 3222 | 3083 | 2782 | 3222 | 3093 | 2814 | 2415 | 1791 | 1332 | 4830 | 4186
| XXS |  | 0.436 | 4480 | 4286 | 3868 | 4480 | 4301 | 3913 | 3387 | 2559 | 1903 | 6598 | 5718
2 1/2" | STD | 40 | 0.203 | 1217 | 1164 | 1051 | 1217 | 1168 | 1063 | 900 | 649 | 482 | 1934 | 1676
| XS | 80 | 0.276 | 1942 | 1858 | 1677 | 1942 | 1864 | 1696 | 1443 | 1051 | 781 | 2955 | 2561
|  | 160 | 0.375 | 2960 | 2831 | 2555 | 2960 | 2841 | 2585 | 2214 | 1636 | 1216 | 4404 | 3817
| XXS |  | 0.552 | 4934 | 4720 | 4260 | 4934 | 4737 | 4309 | 3741 | 2847 | 2117 | 7193 | 6234
3" | STD | 40 | 0.216 | 1094 | 1046 | 944 | 1094 | 1050 | 955 | 808 | 582 | 432 | 1722 | 1492
| XS | 80 | 0.3 | 1768 | 1692 | 1527 | 1768 | 1698 | 1544 | 1312 | 953 | 709 | 2680 | 2322
|  | 160 | 0.438 | 2939 | 2812 | 2538 | 2939 | 2822 | 2567 | 2199 | 1624 | 1208 | 4328 | 3751
| XXS |  | 0.6 | 4407 | 4216 | 3804 | 4407 | 4230 | 3848 | 3329 | 2513 | 1869 | 6395 | 5542
3 1/2" | STD | 40 | 0.226 | 1025 | 980 | 885 | 1025 | 984 | 895 | 757 | 544 | 405 | 1598 | 1385
| XS | 80 | 0.318 | 1669 | 1596 | 1440 | 1669 | 1602 | 1457 | 1237 | 898 | 667 | 2512 | 2177
| XXS |  | 0.636 | 4093 | 3915 | 3533 | 4093 | 3929 | 3574 | 3086 | 2318 | 1724 | 5918 | 5129
4" | STD | 40 | 0.237 | 1433 | 1371 | 1237 | 1433 | 1375 | 1251 | 1061 | 767 | 570 | 1512 | 1310
| XS | 80 | 0.337 | 2076 | 1986 | 1792 | 2076 | 1993 | 1813 | 1543 | 1126 | 837 | 2390 | 2071
|  | 120 | 0.438 | 2740 | 2621 | 2365 | 2740 | 2630 | 2393 | 2047 | 1507 | 1121 | 3305 | 2865
|  | 160 | 0.531 | 3379 | 3233 | 2917 | 3379 | 3244 | 2951 | 2535 | 1885 | 1401 | 4177 | 3620
| XXS |  | 0.674 | 4394 | 4203 | 3793 | 4394 | 4218 | 3837 | 3319 | 2505 | 1863 | 5573 | 4830
5" | STD | 40 | 0.258 | 1259 | 1205 | 1087 | 1259 | 1209 | 1100 | 931 | 672 | 500 | 1361 | 1179
| XS | 80 | 0.375 | 1856 | 1776 | 1602 | 1856 | 1782 | 1621 | 1378 | 1002 | 745 | 2188 | 1896
|  | 120 | 0.5 | 2520 | 2411 | 2176 | 2520 | 2419 | 2201 | 1880 | 1380 | 1026 | 3098 | 2685
|  | 160 | 0.625 | 3201 | 3062 | 2764 | 3201 | 3073 | 2796 | 2399 | 1778 | 1322 | 4040 | 3502
| XXS |  | 0.75 | 3905 | 3736 | 3372 | 3905 | 3749 | 3411 | 2940 | 2203 | 1638 | 5015 | 4346
6" | STD | 40 | 0.28 | 1143 | 1094 | 987 | 1143 | 1097 | 998 | 845 | 608 | 452 | 1266 | 1097
| XS | 80 | 0.432 | 1793 | 1715 | 1548 | 1793 | 1721 | 1566 | 1331 | 967 | 719 | 2165 | 1876
|  | 120 | 0.562 | 2368 | 2266 | 2045 | 2368 | 2273 | 2068 | 1765 | 1293 | 961 | 2959 | 2564
|  | 160 | 0.719 | 3082 | 2948 | 2661 | 3082 | 2959 | 2692 | 2308 | 1708 | 1270 | 3941 | 3416
| XXS |  | 0.864 | 3767 | 3604 | 3252 | 3767 | 3616 | 3290 | 2834 | 2118 | 1575 | 4893 | 4241
8" |  | 20 | 0.25 | 777 | 744 | 671 | 777 | 746 | 679 | 573 | 411 | 305 | 836 | 724
|  | 30 | 0.277 | 861 | 824 | 743 | 861 | 827 | 752 | 635 | 456 | 339 | 953 | 826
| STD | 40 | 0.322 | 1007 | 963 | 869 | 1007 | 967 | 880 | 744 | 534 | 397 | 1153 | 999
|  | 60 | 0.406 | 1277 | 1221 | 1102 | 1277 | 1226 | 1115 | 944 | 681 | 507 | 1529 | 1325
| XS | 80 | 0.5 | 1588 | 1519 | 1371 | 1588 | 1524 | 1387 | 1177 | 853 | 634 | 1957 | 1696
|  | 100 | 0.594 | 1896 | 1814 | 1637 | 1896 | 1820 | 1656 | 1408 | 1025 | 762 | 2388 | 2069
|  | 120 | 0.719 | 2323 | 2222 | 2006 | 2323 | 2230 | 2029 | 1730 | 1267 | 942 | 2976 | 2579
|  | 140 | 0.812 | 2643 | 2529 | 2282 | 2643 | 2537 | 2308 | 1973 | 1451 | 1079 | 3427 | 2970
| XXS |  | 0.875 | 2868 | 2743 | 2476 | 2868 | 2753 | 2504 | 2144 | 1582 | 1176 | 3732 | 3234
|  | 160 | 0.906 | 2977 | 2848 | 2570 | 2977 | 2858 | 2600 | 2227 | 1646 | 1224 | 3885 | 3367
10" |  | 20 | 0.25 | 621 | 594 | 536 | 621 | 596 | 543 | 458 | 327 | 243 | 668 | 579
|  | 30 | 0.307 | 766 | 733 | 661 | 766 | 735 | 669 | 565 | 405 | 301 | 867 | 752
| STD | 40 | 0.365 | 912 | 872 | 787 | 912 | 875 | 796 | 673 | 483 | 359 | 1073 | 930
|  | 60 | 0.5 | 1263 | 1209 | 1091 | 1263 | 1213 | 1103 | 934 | 674 | 501 | 1558 | 1350
| XS | 80 | 0.594 | 1507 | 1441 | 1301 | 1507 | 1446 | 1316 | 1116 | 808 | 601 | 1898 | 1645
|  | 100 | 0.719 | 1842 | 1762 | 1590 | 1842 | 1768 | 1608 | 1367 | 994 | 739 | 2360 | 2046
|  | 120 | 0.844 | 2179 | 2085 | 1881 | 2179 | 2092 | 1903 | 1622 | 1185 | 881 | 2831 | 2453
| XXS | 140 | 1 | 2612 | 2499 | 2255 | 2612 | 2507 | 2281 | 1949 | 1433 | 1066 | 3434 | 2976
|  | 160 | 1.125 | 2963 | 2835 | 2558 | 2963 | 2845 | 2588 | 2217 | 1638 | 1218 | 3923 | 3400
12" |  | 20 | 0.25 | 522 | 500 | 451 | 522 | 502 | 456 | 384 | 275 | 204 | 563 | 488
|  | 30 | 0.33 | 693 | 663 | 598 | 693 | 665 | 605 | 510 | 365 | 272 | 798 | 692
| STD |  | 0.375 | 788 | 754 | 680 | 788 | 756 | 688 | 581 | 416 | 310 | 932 | 808
|  | 40 | 0.406 | 854 | 817 | 738 | 854 | 820 | 746 | 630 | 452 | 336 | 1025 | 888
| XS |  | 0.5 | 1060 | 1014 | 915 | 1060 | 1017 | 925 | 783 | 563 | 419 | 1308 | 1134
|  | 60 | 0.562 | 1195 | 1143 | 1031 | 1195 | 1147 | 1043 | 883 | 636 | 473 | 1497 | 1298
|  | 80 | 0.688 | 1470 | 1406 | 1269 | 1470 | 1411 | 1283 | 1088 | 787 | 585 | 1880 | 1629
| XXS | 100 | 0.844 | 1821 | 1742 | 1572 | 1821 | 1748 | 1590 | 1352 | 983 | 731 | 2367 | 2051
|  | 120 | 1 | 2178 | 2084 | 1881 | 2178 | 2091 | 1902 | 1621 | 1184 | 881 | 2867 | 2484
|  | 140 | 1.125 | 2467 | 2361 | 2130 | 2467 | 2369 | 2155 | 1840 | 1350 | 1004 | 3270 | 2834
|  | 160 | 1.312 | 2911 | 2785 | 2513 | 2911 | 2794 | 2542 | 2177 | 1607 | 1195 | 3885 | 3367
14" |  | 10 | 0.25 | 475 | 455 | 410 | 475 | 456 | 415 | 350 | 249 | 186 | 510 | 442
|  | 20 | 0.312 | 594 | 569 | 513 | 594 | 571 | 519 | 438 | 313 | 233 | 678 | 588
| STD | 30 | 0.375 | 716 | 685 | 618 | 716 | 688 | 626 | 528 | 378 | 281 | 848 | 735
|  | 40 | 0.438 | 839 | 803 | 724 | 839 | 806 | 733 | 619 | 444 | 330 | 1019 | 883
| XS |  | 0.5 | 963 | 921 | 831 | 963 | 924 | 841 | 711 | 510 | 380 | 1189 | 1030
|  | 60 | 0.594 | 1146 | 1097 | 990 | 1146 | 1100 | 1001 | 847 | 610 | 454 | 1445 | 1252
|  | 80 | 0.75 | 1460 | 1397 | 1261 | 1460 | 1402 | 1275 | 1082 | 782 | 582 | 1884 | 1633
|  | 100 | 0.938 | 1843 | 1764 | 1591 | 1843 | 1770 | 1610 | 1369 | 995 | 740 | 2415 | 2093
|  | 120 | 1.094 | 2167 | 2073 | 1871 | 2167 | 2080 | 1893 | 1612 | 1178 | 876 | 2869 | 2486
|  | 140 | 1.25 | 2500 | 2392 | 2159 | 2500 | 2400 | 2184 | 1865 | 1369 | 1018 | 3331 | 2887
|  | 160 | 1.406 | 2835 | 2712 | 2448 | 2835 | 2722 | 2476 | 2119 | 1563 | 1162 | 3797 | 3291
16" |  | 10 | 0.25 | 415 | 397 | 358 | 415 | 399 | 363 | 305 | 218 | 162 | 447 | 388
|  | 20 | 0.312 | 519 | 496 | 448 | 519 | 498 | 453 | 382 | 273 | 203 | 592 | 513
| STD | 30 | 0.375 | 625 | 598 | 540 | 625 | 600 | 546 | 460 | 329 | 245 | 741 | 642
| XS | 40 | 0.5 | 840 | 803 | 725 | 840 | 806 | 733 | 619 | 444 | 330 | 1037 | 899
|  | 60 | 0.656 | 1108 | 1060 | 957 | 1108 | 1064 | 968 | 819 | 589 | 438 | 1413 | 1225
|  | 80 | 0.844 | 1437 | 1375 | 1240 | 1437 | 1379 | 1255 | 1064 | 769 | 572 | 1869 | 1620
|  | 100 | 1.031 | 1771 | 1694 | 1529 | 1771 | 1700 | 1547 | 1314 | 955 | 710 | 2337 | 2026
|  | 120 | 1.219 | 2111 | 2020 | 1823 | 2111 | 2027 | 1844 | 1570 | 1146 | 852 | 2810 | 2435
|  | 140 | 1.438 | 2517 | 2408 | 2173 | 2517 | 2417 | 2198 | 1877 | 1378 | 1025 | 3375 | 2925
|  | 160 | 1.594 | 2810 | 2688 | 2426 | 2810 | 2697 | 2454 | 2100 | 1548 | 1151 | 3782 | 3278
18" |  | 10 | 0.25 | 369 | 353 | 318 | 369 | 354 | 322 | 271 | 193 | 144 | 397 | 344
|  | 20 | 0.312 | 461 | 441 | 398 | 461 | 442 | 402 | 339 | 242 | 180 | 525 | 455
| STD |  | 0.375 | 555 | 531 | 479 | 555 | 533 | 484 | 408 | 292 | 217 | 657 | 570
|  | 30 | 0.438 | 649 | 621 | 561 | 649 | 623 | 567 | 478 | 342 | 254 | 790 | 684
| XS |  | 0.5 | 744 | 712 | 643 | 744 | 715 | 650 | 549 | 393 | 292 | 920 | 797
|  | 40 | 0.562 | 838 | 802 | 724 | 838 | 805 | 732 | 618 | 443 | 330 | 1052 | 912
|  | 60 | 0.75 | 1126 | 1077 | 972 | 1126 | 1081 | 983 | 832 | 599 | 445 | 1453 | 1259
|  | 80 | 0.938 | 1418 | 1357 | 1224 | 1418 | 1362 | 1239 | 1050 | 759 | 564 | 1861 | 1613
|  | 100 | 1.156 | 1766 | 1690 | 1525 | 1766 | 1696 | 1542 | 1311 | 952 | 708 | 2344 | 2031
|  | 120 | 1.375 | 2118 | 2027 | 1829 | 2118 | 2034 | 1850 | 1576 | 1150 | 855 | 2835 | 2457
|  | 140 | 1.562 | 2426 | 2321 | 2094 | 2426 | 2329 | 2118 | 1808 | 1326 | 986 | 3263 | 2828
|  | 160 | 1.781 | 2790 | 2669 | 2408 | 2790 | 2678 | 2436 | 2085 | 1536 | 1142 | 3772 | 3269
20" |  | 10 | 0.25 | 331 | 317 | 286 | 331 | 318 | 298 | 244 | 173 | 129 | 357 | 309
| STD | 20 | 0.375 | 499 | 477 | 430 | 499 | 479 | 435 | 367 | 262 | 195 | 590 | 511
| XS | 30 | 0.5 | 669 | 640 | 577 | 669 | 642 | 584 | 493 | 352 | 262 | 827 | 717
|  | 40 | 0.594 | 795 | 761 | 686 | 795 | 763 | 694 | 586 | 420 | 312 | 1004 | 870
|  | 60 | 0.812 | 1096 | 1049 | 946 | 1096 | 1052 | 957 | 810 | 583 | 433 | 1424 | 1234
|  | 80 | 1.031 | 1404 | 1343 | 1212 | 1404 | 1348 | 1226 | 1039 | 751 | 558 | 1852 | 1605
|  | 100 | 1.281 | 1760 | 1684 | 1520 | 1760 | 1690 | 1537 | 1306 | 949 | 706 | 2350 | 2037
|  | 120 | 1.5 | 2077 | 1987 | 1793 | 2077 | 1994 | 1814 | 1545 | 1127 | 838 | 2793 | 2421
|  | 140 | 1.75 | 2446 | 2340 | 2112 | 2446 | 2348 | 2136 | 1824 | 1337 | 995 | 3308 | 2867
|  | 160 | 1.969 | 2774 | 2654 | 2395 | 2774 | 2663 | 2423 | 2073 | 1527 | 1136 | 3763 | 3261
24" |  | 10 | 0.25 | 276 | 264 | 238 | 276 | 265 | 241 | 203 | 144 | 107 | 296 | 257
| STD | 20 | 0.375 | 415 | 397 | 358 | 415 | 398 | 362 | 305 | 217 | 162 | 491 | 426
| XS |  | 0.5 | 556 | 532 | 480 | 556 | 533 | 485 | 409 | 292 | 217 | 687 | 595
|  | 30 | 0.562 | 625 | 598 | 540 | 625 | 600 | 546 | 460 | 329 | 245 | 785 | 681
|  | 40 | 0.688 | 767 | 733 | 662 | 767 | 736 | 669 | 565 | 405 | 301 | 983 | 852
|  | 60 | 0.969 | 1089 | 1042 | 941 | 1089 | 1046 | 951 | 805 | 579 | 431 | 1432 | 1241
|  | 80 | 1.219 | 1382 | 1322 | 1193 | 1382 | 1326 | 1207 | 1023 | 739 | 549 | 1840 | 1594
|  | 100 | 1.531 | 1753 | 1677 | 1514 | 1753 | 1683 | 1531 | 1301 | 945 | 703 | 2358 | 2044
|  | 120 | 1.812 | 2093 | 2003 | 1807 | 2093 | 2009 | 1828 | 1557 | 1136 | 845 | 2833 | 2455
|  | 140 | 2.062 | 2399 | 2295 | 2071 | 2399 | 2303 | 2095 | 1788 | 1310 | 974 | 3261 | 2826
|  | 160 | 2.344 | 2750 | 2631 | 2374 | 2750 | 2640 | 2402 | 2055 | 1513 | 1125 | 3751 | 3251
Values are expressed in psi. No allowance for corrosion or erosion is provided in the working pressures listed herein. If either is expected, the amount of inches should be calculated and reduced working pressures should be calculated.
Working pressures for A-106-B and A-234WPB may also be used for: (1) A-53-B pipe as shown, (2) A-106-A or A-53-A pipe or A-234-WPA fittings after multiplying the above values by .800 at 650 deg. F & lower, .812 at 700 deg. F, .826 at 750 deg. F, (3) A-106-C pipe or A-234-WPC fittings after multiplying the above values by 1.17 at 650 deg. F & lower, 1.16 at 700 deg. F, 1.14 at 750 deg. F
Central Coast Piping Products takes no responsibility for the contents of these charts and their applications. The content of this Web site is provided "As Is", As Available". Central Coast Piping Products is not responsible for any misuse or misapplication of this information. We provide informational charts as a reference guide only; all engineering calculations are the responsibility of the reader, purchaser and/or end user.